SECTION 260943

NETWORK LIGHTING CONTROL SYSTEM

Rev210-RP-QC-2600

# PART 1 - GENERAL	(Digital Relay Panels)

## SUMMARY

### The work covered in this section is subject to all of the requirements in the General Conditions of the Specifications.  Contractor shall coordinate all of the work in this section with all of the trades covered in other sections of the specification to provide a complete and operable system.  All Labor, materials, appliances, tools, equipment, facilities, transportation and services necessary for and incidental to performing all operations in connection with furnishing, delivery and installation of the work of this Section.

## DESCRIPTION OF WORK

### Furnish and install a complete system for the control of lighting and other equipment as indicated on the plans, detailed in the manufacturer submittal and as further defined herein.  Contractor is solely responsible to verify quantity, installation locations and wiring requirements for this project.  Specific manufacturer’s catalog numbers, when listed in this section are for reference only.  It is the responsibility of the contractor to verify with lighting control manufacturer all catalog information and specific product acceptability.

### The system shall include but not be limited by the following list: Pre-wired, microprocessor controlled relay or dimming panels with latching relays controlled via a complete list of communication based accessories including digital switches, digital photocells, digital SmartBreaker panelboards, Digital Time Clock (DTC) and interface cards to dimming systems, building automation systems, thermostats, and other devices.  The type of lighting control equipment and wiring specified in this section is covered by the description: Microprocessor Controlled Digital Lighting Control system with RS 485 Bus communications.  Requirements are indicated elsewhere in these specifications for work including, but not limited to, raceways and electrical boxes and fittings required for installation of control equipment and wiring.  They are not the work of this section.

1.2.3	SmartBreaker panel boards shall operate as if each breaker were a relay in the lighting control system. All references in this spec to the operation of relays shall apply equally to the solenoid operated thermal magnetic breakers within SmartBreaker panel boards.

## SUBMITTALS

### Section 16010 – Shop Drawing Requirements.

### Shop Drawings: Submit dimensioned drawings of lighting control system and accessories including, but not necessarily limited to, relay panels, switches, DTC, photocells and other interfaces.  Shop drawings shall indicate exact location of each device or a RFI to confirm location.  Plans are floor plan diagrams.  EC to verify all lighting control material requirements from approved shop drawings. “Cut Sheet” submittal not acceptable.

### Product Data: Submit for approval manufacturer's data on the specific lighting control system and components.  Submittal shall be electronic format with hard copy available.  To prevent departures from approved system operation, electronic files submitted shall be able to be directly downloaded to the specified system at manufacturer facility. Submit a complete bill of materials with part numbers, description and voltage specifications.

### Manufacturer shall provide free software that can be used to specify the system, detail all programming and generate a single line in a format that can be dropped into industry standard CAD packages.

### One Line Diagram: Submit a one-line diagram of the system configuration indicating the type, size and number of conductors between each component if it differs from that illustrated in the riser diagram in these specifications.  Submittals that show typical riser diagrams are not acceptable.

## QUALITY ASSURANCE

### Products shall be manufactured by Lighting Control & Design, Los Angeles, CA, 800.345.4448 or approved equal.  Such firms shall be regularly engaged in manufacturing of lighting control equipment and ancillary equipment, of types and capacities required, whose products have been in satisfactory use in similar service for not less than 5 years. Any product other than those listed in this specification must be pre-approved a minimum of two weeks before bid time. No exceptions.

### Control wiring shall be in accordance with the NEC requirements for Class 2 remote control systems, Article 725 and manufacturer specification.

### A licensed electrician shall functionally test each system component after installation, verify proper operation and confirm that all relay and dimming panels and switch wiring conform to the wiring documentation.  The Electrical Contractor (EC) is required to phone LC&D a minimum of 7 days before turnover for system checkout.  At time of LC&D contact, all components including phone line to modem must be installed, powered and operational.

### Comply with NEC and all local and state codes as applicable to electrical wiring work.

### Lighting control panels shall be UL 916 Listed.  LCPs controlling emergency circuits shall be ETL listed to UL 924.  Relay panels shall also be listed to comply with CSA C22.2#205 Emergency source circuits controlled in normal operation by a relay panel shall fully comply with NEC 700-9(b).  Electrical contractor is responsible for verifying compliance.

### The lighting control system shall be listed, approved and comply as required with all national, state and local energy codes to include but not limited to California Title 24 and ASHRAE 90.1-2004.

## MAINTENANCE MATERIALS

### Division 1 - Execution Requirements: Spare parts and maintenance products.

### Provide 10% spare relays per LCP, up to the maximum capacity of the LCP.

### Provide CD version of manufacturers operating software to include graphical interface software.

### Provide 2 extra sets of as-built and operating manuals.

## SUBSTITUTIONS

### Substitutions are permitted as voluntary alternates.  Base bid must reflect the specified equipment.

##### 1.6.2	A product must go through the following process before being approved as a substitution:

##### 1.6.2.1	A list of substitutions shall be provided to the owner as an attachment to the bid form.  Submit along with bill of material, CD of proposed operating system, and a one line diagram of the system configuration proposed indicating the type, size and number of conductors between each component if it differs from that illustrated in the riser diagram or in these specifications.

##### 1.6.2.2	The list will be reviewed by the owner and the engineer to determine whether the equipment meet the project needs.  A $500 retainer will be submitted with the list of voluntary alternates to cover this meeting.  If the owner and engineer agree that this meeting is not required, then the $500 will be returned to the contractor.

##### 1.6.2.3	The retainer is for evaluation of the alternate.  The retainer is to be used to cover the time spent in this evaluation.  The fee will be collected based on time spent in evaluation, not on whether the alternate is accepted.  All unused portions will be returned to the contractor with an invoice marked “paid” by the engineer, architect, and/or owner.

# 1.7	SYSTEM DESCRIPTION

## The lighting control system is a networked system that communicates via RS485. The system must be able to communicate with fully digital centralized relay panels, small distributed relay panels (Available with 0-10Volt dimming outputs), (also called Micro Panels), Fully distributed fixture level control by bus connected relays or dimmers, (also called X-Point)  smart breaker panels, digital switches, photocells, various interfaces and  operational software.  The intent of the specification is to integrate all lighting control into one system.  Distributed lighting control shall be provided using networked micro relay panels or bus connected fixture level control (X Point.).  Lighting control system shall include all hardware and software.  Software shall be resident within the lighting control system.  System shall provide local access to all programming functions at the master LCP and remote access to all programming functions via dial up modem and through any standard computer workstation.  Lighting control system shall have the capability to be remotely controlled via the internet or building wide Ethernet LAN.  Desktop computers are not part of this section and will be provided by others.

## System software shall provide real time status of each relay, each zone and each group.

## Lighting control system shall be able to be monitored by and take commands from a remote PC.  At any time, should the remote PC go off-line all system programming uploaded to the lighting control system shall continue to operate as intended.  Systems requiring an on line PC or server for normal operation are not acceptable

## All devices shall be pre-addressed at the factory. If required by the client the system may be specified without pre-addressing and simple software is to be provided to simplify addressing in place. This particularly applies to fixture level control where controls may be factory mounted on the fixture in advance to speed installation.

## All programs, schedules, time of day, etc, shall be held in non-volatile memory for an indefinite time exceeding 10 years in the event of power failure. At restoration of power, lighting control system shall implement programs required by current time and date. Time of day shall be battery backed for at least 10 years.

## System shall be capable of warning of an impending off sweep by flashing lights Off/On once or twice (programmable) by relay or by zone prior to the lights being turned off.  The warning interval times between the flash and the final lights off signal shall be definable for each zone.  Additionally an audible signal shall be able to be programmed that gives a mild note on the first flash and a more insistent signal on the second one. Occupant shall be able to override any scheduled Off sweep using local wall switches within the occupied space.  Occupant override time shall be locally and remotely programmable and not exceed 2-hours.

## The system shall be capable of implementing On commands, Off commands, Raise (dimming) commands, Lower (dimming) commands for any relay, group or zone by means of digital wall switches, contact closure switches, time clock schedules including offsets from dusk and dawn by up to 10 hours, photocell, pc software or other devices connected to programmable inputs in a lighting control panel.

## The lighting control system shall provide the ability to control each relay and each relay group per this specifications requirement.  All programming and scheduling shall be able to be done locally at the master LCP and remotely via dial up modem or via the Internet. Remote connection to the lighting control system shall provide real time control and real time feedback.

## Micro relay panels shall be capable of taking inputs from contact closure switches and outputting up to 8 independent 0v to 10v dimming signals.  All micro relay panels and all devices connected to micro relay panels (switches, photocells and occupancy sensors, etc) shall be wired per lighting control manufacturers instructions.

## X Point relay or dimming modules shall be fed from an X Point router that sits on the GR 2400 Bus in the manner of a relay panel. Individual modules are fed from this panel on a separate bus. Each router may feed two strings of up to 64 modules on a 2000ft string. Each Module may be a single relay, a dual relay or a dimming (0-10Volt) module. Relays in the modules are to be capable of being separately controlled in the same manner as an individual relay or dimmer in a relay or dimmer panel.  Additionally multiple relays may be collected together to act together as a single multi-pole load or dimmer for ease of programming. Graphical software shall be available that does these assignments and reassignments in a straightforward and logical manner. Relays shall have the same specifications as laid out in 2.1.3.  Modules with reduced current ratings may be supplied with Quick Connect connectors for more rapid installation.

# PART 2 - PRODUCTS

### MATERIAL AND COMPONENTS

### Relay Panels:

### All LCP’s shall be in NEMA 1 rated enclosure with screw cover or hinged Locking door.  Other NEMA rated types optional.

### A barrier shall separate the high voltage and low voltage compartments of the panel and separate 120v and 277v.

### LCP input power shall be capable of accepting 120v or 277v without rewiring or 120 or 347Volts for Canadian applications.

### Control electronics in the low voltage section shall be capable of driving 2 to 48 relays (rated as per Section 2.1.3), control any individual or group of relays, provide individual relay overrides, provide a master override for each panel, store all programming in non-volatile memory, after power is restored return system to the correct state for time of day, provide programmable dual blink warn timers for each relay or zone of relays, and be able to control Normally Open Latching (NOL) or Normally Closed Latching (NCL) relays.

### Lighting control system shall be digital and consist of a Master LCP, Remote LCPs, Micro LCPs with up to 8 individual relays, X Point Router and associated relays or dimmers emulating standard or Micro LCPs, digital switches, digital interface cards and if required, SmartBreaker panelboards.  All system components shall connect and be controlled via Category 5, 4 twisted pair cable with RJ45 connectors, providing real time two-way communication with each system component.  All Micro LCP’s shall provide multiple inputs for photocells and occupancy sensors. Analog systems are not acceptable.

### Micro Relay Panels

### Micro relay panels shall have from 2 to 8 relays (rated as per Section 2.1.3) and shall control all lighting in the designated area indicated on the plans and be part of the lighting control network.  Each micro relay panel shall provide minimum 300ma at 12/24vdc for powering occupancy sensors.  Micro relay panels that require a separate occupancy sensor power pack are not acceptable.

### Micro relay panel shall provide a minimum of 4-programmable photocell inputs, a minimum of 8-programmable occupancy sensor contact closure inputs.  This requirement is to insure integration of entire lighting system into one networked, lighting control system.

### Micro relay panels shall be capable of outputting a minimum of 4 and up to 8 independent 0v to 10v dimming signals, one independent dimming signal per relay for each of 8 relays.  In order to maximize daylight harvesting and minimize disruption to occupants, each dimming output shall provide adjustment for baseline, start point, mid point, end point, trim, fade up rate, fade down rate, time delay and enable/disable masking. All photocell settings must be remotely accessible.  Systems providing On, Off with Time Delay only, and system that do not provide remote access are not acceptable.

### MicroPanels shall have built in capability to take commands from a fully compatible wireless switch. Wireless switch shall contain no battery; have 32-bit unique ID and a minimum 90-foot range line of sight.

##### Standard Output relays

##### UL Listed 30 Amp @ 277VAC Ballast and HID and 20 Amp Tungsten at 120 Vac. 347V Ballast and HID at 20 amps Latching Relay wit 18,000A SCCR at 277Vac,

##### Relays shall be individually replaceable. Relay terminal blocks shall be capable of accepting two (2) #8AWG wires on both the line and the load side. Systems that do not allow for individual relay replacement or additions are not acceptable. Relays to be rated for 250,000 operations minimum at a full 30a lighting load. Standard relay shall default to closed at normal power loss, Normally Closed Latching (NCL).

##### Optional relay types available shall include: Normally Open Latching (NOL) relay rated for 250,000 operations, a 600v 2-pole NO and NC and a Single Pole, Double Throw (SPDT) relay.

##### Low Voltage Switches

##### All switches shall be digital and communicate via RS 485. Contact closure style switches, except as specified for connection to the micro relay panel programmable contact closure inputs, shall not be acceptable. The programming for a digital switch shall reside in the switch itself, via double EPROM memory.  Any digital switch button function shall be able to be changed locally (at the DTC or a PC) or remotely, via modem, Internet or Ethernet.

##### Digital low voltage switch shall be a device that sits on the lighting control system bus.  Digital switch shall connect to the system bus using the same cable and connection method required for relay panels.  Each button shall be capable of being programmed for On only, Off only, Mix (Some on some off), On/Off (toggle), Raise (Dim up) and Lower (Dim down).  Further each button shall be able to be enabled or disabled over the bus. An audible alarm shall be available on all switches that can be programmed to beep on button push or with warning light blinks.

##### Keyed switches shall be similarly programmable and connect to the lighting control system bus.

##### Digital switches for high abuse areas (common areas, gymnasiums, etc.) shall be vandal resistant, contain no moving parts, and be touch sensitive and available with up to two buttons in a single gang. Multi gang versions shall also be available. Touch pads shall be Stainless Steel and capable of handling both high abuse and wash down locations. High abuse switches shall connect to the lighting control system digital bus. Each high abuse touch button shall be able to be programmed in the same way as other digital switch buttons. Switches must be capable of handling electrostatic discharges of at least 30,000 volts (1cmspark) without any interruption or failure in operation.

##### Wireless Switches-System shall have the capability to accept inputs from 32-bit unique ID wireless switches. Wireless switches shall have no battery and be capable of On, Off, Raise and Lower commands. Wireless switches shall have a minimum 90 foot line of sight range

##### DTC - Digital Electronic Time Clock

##### A Digital Time Clock (DTC) shall control and program the entire lighting control system and supply all time functions and accept modem (RS232) inputs.

##### DTC shall be capable of up to 32 schedules. Each schedule shall consist of one set of On and Off times per day for each day of the week and for each of two holiday lists. The schedules shall apply to any individual relay or group of relays.

##### The DTC shall be capable of controlling digital devices at up to 127 addresses on a single bus and capable of interfacing digitally with other buses using manufacturer supplied interface cards.

##### The DTC shall accept control locally using built in button prompts and use of an 8 line 21-space display or from a computer or modem via an on-board RS 232 port. All commands shall be in plain English. The DTC shall be run from non-volatile memory so that all system programming is retained indefinitely and time of day is battery backed for up to 10 years.

##### Unity™ lighting control software shall provide via local or remote PC a visual representation of each device on the bus, show real time status and the ability to change the status of any individual device, relay or zone.   System shall be capable of running optional Unity GX lighting control software. Unity GX shall provide for importing vector based graphics and a simple interface that allows users or a factory programmer to overlay color “controls” that are associated with relays or collections of relays. Clicking on the overlays changes the color and the status of the relays for visual display of large systems.

##### System shall come with a pre-Installed modem that allows for remote programming from any location using a PC and free remote control software.

##### DTC shall provide system wide timed overrides.  Any relay, group or zone that is overridden ON, before or after hours, shall automatically be swept OFF by the DTC a maximum of 2 hours later.

##### PHOTOCELL: Photocells to be mounted in location indicated on the plans.  Photocells used for exterior lights shall provide multiple trip points from 1 roof mounted unit. All trip points shall be able to be changed remotely via Internet or dial up modem. Photocells requiring manual trip point adjustment are not acceptable.  Photocell used for interior lighting control shall have multiple settings such as start-point, mid-point, off-point, fade-up, fade-down, etc.  All settings shall be remotely accessible and adjustable.  Systems providing local adjustment only are not acceptable.  Photocells to be certified to comply with the current energy code covering this project at time of submittal of plans for building permit.

##### Interfaces: For future expansion capability, systems are to have available all of the following interfaces.  Verify and install only those interfaces indicated on the plans.

##### A dry contact input interface card that provides 14 programmable dry contact closure inputs. Use shielded cable to connect input devices to interface card on runs over 200ft.

##### Uplink Interface card that allows a single bus to be part of a greater system connected together by a Back Bone Bus. The back Bone bus requires a server for the Modem and Ethernet connections to such a large system.

##### An interface card (T-LINK) that allows the DTC to control up to 32 digital XCI brand thermostats.  Programming of thermostats is to be capable of being done locally (at the DTC) or remotely, via modem, Internet or Ethernet.

##### When Unity GX software is specified full graphic pages shall be designed to the owner’s specifications.  Owner is to provide to manufacturer all necessary files and criteria.  Provide ____ GX pages.

##### Direct digital interface to SmartBreaker panelboards.  Relay panel and SmartBreaker panelboard circuits shall appear on the system software as similar, yet distinct, items and maintain all functions and features of the system software.

##### Direct digital interface to DMX 512 based systems. DMX interface shall provide 14 global commands, each of which can be modified locally or remotely using lighting controls manufacturer supplied software.  DMX interface shall be integral to the system bus and shall connect and be controlled via a single Category 5, 4 twisted pair cable, providing real time response from the lighting control system to DMX commands.

##### Direct digital interface to building automation systems using DDC protocols such as BACnet, Metasys (N2) and ModBus that accept on/off commands, time schedules and report status of all relays in all panels in real time.  Interface cards shall “self populate” each individual relay and each group to the BAS. All BAS system programming required shall be the responsibility of the BAS system provider.

# PART 3 - EXECUTION

#### EQUIPMENT INSTALLATION

#### Mount relay control cabinets adjacent to respective lighting panel board. Cabinet shall be surface or flush mount, per plans.  Wiring between relay control cabinets and panelboards shall be in accordance with local codes and acceptable industry standards.  Under no circumstances will any extra payment be authorized for the EC or GC due to the EC’s lack of knowledge or understanding of any and all prevailing codes or specified manufacturer’s installation requirements.  Neatly lace and rack wiring in cabinets.  During construction process, protect all interior components of each relay panel and each digital switch from dust and debris.  Any damage done to electronic components due to failure to protect them shall be the sole responsibility of the installing contractor.

#### Switches: Provide outlet boxes, single or multi-gang, as shown on the plans for the low voltage digital switches.  Mount switches as per plans.  Supply faceplates per plans and specifications.  EC is specifically responsible to supply and install the required low voltage cable, Category 5, 4 twisted pair, with RJ45 connectors (commonly referred to as Cat 5 patch cable) between all switches and panels. Field-test all Cat 5 patch cable with a recognized cable tester.  All low voltage wire to be run in conduit, per local codes.

#### Manufacturer to provide on all systems of more than 2 panels a crimping kit with sufficient approved EZ Brand RJ 45 connectors to populate the whole system. A simple manual that shows all the pitfalls of crimping RJ 45s and how to do it right must be both provided and read by the installing contractor.

#### Wiring

#### Do not mix low voltage and high voltage conductors in the same conduit.  No exceptions.

#### Ensure low voltage conduits or control wires do not run parallel to current carrying conduits.

#### Place manufacturer supplied “terminators” at each end of the system bus per manufacturer’s instructions.

#### Plug in Category 5 patch cable with RJ45 end connector that has been field-tested with a recognized cable tester, at the indicated RJ45 connector provided at each lighting control device, per manufacturer’s instructions.

#### Use Category 5 patch cable for all system low voltage connections.  Additional conductors may be required to compensate for voltage drop with specific system designs.  Contact LC&D or refer to the GR2400 manual for further information.  Use shielded cable for dry contact inputs on runs over 200ft.

#### Do not exceed 4000ft-wire length for the system bus.

#### All items on the bus shall be connected in sequence (daisy chained). Star and spur topologies are not acceptable.

#### The specified lighting control system shall be installed by the electrical contractor who shall make all necessary wiring connections to external devices and equipment, to include photocell.  EC to wire per manufacturer instructions.

#### INSTALLATION AND SET-UP

#### Verify that conduit for line voltage wires enters panel in line voltage areas and conduit for low-voltage control wires enters panel in low-voltage areas. Refer to manufacturer's plans and approved shop drawings for location of line and low-voltage areas. This is especially applicable in jobs where back boxes are shipped in advance. It is the responsibility of the contractor to verify with lighting control manufacturer all catalog information and specific product acceptability.

#### For approved contact closure switches, use #18 AWG stranded conductors. For all other digital switches, provide wiring required by system manufacturer.

#### For classroom digital switches provide wiring required by system manufacturer

#### Contractor to test all low voltage cable for integrity and proper operation prior to turn over. Verify with system manufacturer all wiring and testing requirements.

#### Before Substantial Completion, arrange and provide a one-day Owner instruction period to designated Owner personnel. Set-up, commissioning of the lighting control system and Owner instruction includes:

#### Confirmation of entire system operation and communication to each device.

#### Confirmation of operation of individual relays, switches, occupancy sensors and daylight sensors

#### Confirmation of system Programming, photocell settings, override settings, etc.

#### Provide training to cover installation, maintenance, troubleshooting, programming, and repair and operation of the lighting control system.

#### Panels shall be located so that they are readily accessible and not exposed to physical damage.

#### Panel locations shall be furnished with sufficient working space around panels to comply with the National Electric Electrical Code.

#### Panels shall be securely fastened to the mounting surface by at least 4 points.

#### Unused openings in the cabinet shall be effectively closed.

#### Cabinets shall be grounded as specified in the National Electrical Code.

#### Lugs shall be suitable and listed for installation with the conductor being connected.

#### Conductor lengths shall be maintained to a minimum within the wiring gutter space. Conductors shall be long enough to reach the terminal location in a manner that avoids strain on the connecting lugs.

#### Maintain the required bending radius of conductors inside cabinets.

#### Clean cabinets of foreign material such as cement, plaster and paint.

#### Distribute and arrange conductors neatly in the wiring gutters.

#### Follow the manufacturer's torque values to tighten lugs.

#### Before energizing a panel, the following steps shall be taken:

#### Retighten relay connections to the manufacturer's torque specifications.  Verify that required connections have been furnished.

#### Remove shipping blocks from component devices and the panel interior.

#### Remove debris from panel interior.

#### Follow manufacturer’s instructions for installation and all low voltage wiring.

#### Service and Operation Manuals:

#### Submit operation and service manuals.  Complete manuals shall be bound in flexible binders and data shall be typewritten or drafted.

#### Manuals shall include instructions necessary for proper operation and servicing of system and shall include complete wiring circuit diagrams of system, wiring destination schedules for circuits and replacement part numbers.  Manuals shall include as-built cable Project site plot plans and floor plans indicating cables, both underground and in each building with conduit, and as-built color coding used on cables. Programming forms of systems shall be submitted with complete information.

#### Comply with energy code lighting control system “Acceptance Requirements”. Acceptance tests are used to verify that lighting controls were installed and calibrated correctly. These tests may require that a responsible party certify that controls are installed and calibrated properly. This is the installing contractor’s responsibility.  Verify requirements with building authority.

#### DOCUMENTATION

#### Each relay shall have an identification label indicating the originating branch circuit number and panelboard name as indicated on the drawings. Each line side branch circuit conductor shall have an identification tag indicating the branch circuit number.

#### Provide a point-to-point wiring diagram for the entire lighting control system.  Diagram must indicate exact mounting location of each system device.  This accurate “as built” shall indicate the loads controlled by each relay and the identification number for that relay, placement of switches and location of photocell.  Original to be given to owner, copies placed inside the door of each LCP.

#### SERVICE AND SUPPORT

#### Start Up: EC shall contact LC&D at least 7 days before turnover of project.  LC&D will remotely dial into the lighting control system, run diagnostics and confirm system programming.  EC shall be available at the time of dial in to perform any corrections required by LC&D.   EC is responsible for coordinating with GC and the owner the installation of a dedicated telephone line or a shared phone line with an automatic Fax/Modem switch.  Phone jack to be mounted within 12” of Master LCP.  Label jack with phone number.  EC to connect phone line from jack to Master LCP.

#### Telephone factory support shall be available at no additional cost to the EC or Owner both during and after the warranty period.  Factory to pre-program the lighting control system per plans and approved submittal, to the extent data is available.  Upon request manufacturer to provide remote dial up software at no added cost to system owner.   No exceptions.

#### Provide a factory technician for on-site training of the owners’ representatives and maintenance personnel.  Coordinate timing with General Contractor.  Provide ___ days of factory on-site training.

#### CLEANING

#### Division 1 - Execution Requirements: Final cleaning.

#### Clean photocell lens as recommended by manufacturer.

#### Clean all switch faceplates.

- END OF SECTION